## Cover
Water Meter Sizing Form
One Form Per Meter
Preparer's Information: |  | Project Information: |  | Date ====>
Name ============> |  | Permit or AR Number
Title ==============> |  | Name of Project ===>
Company=========> |  | Project Address ===>
Address ==========>
Phone ============>
Email Address =====>
Please Note:
1. All commercial facilities must be metered separately from residential facilities with the exception of those commercial facilities that are within a master metered residential development and designed for the exclusive use of the residents within such development.
2. The Design Engineer/Architect must submit signed and sealed documentation supporting meter sizing. Sizing shall be based upon fixture flow values, as shown on the following page and the table on page 3, unless approved otherwise by Utility Deviation. If an increase in meter size is requested to accommodate for fire flow, the Engineer/Architect should check appropriate box below. A Utility Deviation will not be required for increasing meter size for fire flow requirements. For all meter sizes, the Engineer/Architect must consider all relevant factors before selecting the final meter size.
3. For remodeling projects this form must be submitted only if there is a net increase in fixture flow value.
This Section to be filled out by Engineer/Architect of Record:
Demand in accordance with the Fixture Flow Value Worksheet and the Table for Estimating Demand |  | Meter Size Required:
| GPM | Meter Size Requested:
Existing Meter Size:
If the meter size requested is larger than the meter size required per the table velow, please indicate the reason for the request by checking the appropriate box:
|  |  | Demand Range (GPM) | Meter Size
|  |  | 0 to 30 | 3/4"
|  |  | 30.1 to 50 | 1"
Type or Print Name of Engineer/Architect of Record for Project |  |  | 50.1 to 100 | 1 1/2"
|  |  | 100.1 to 160 | 2"
|  |  | 160.1 to 450 | 3"
|  |  | 450.1 to 1000 | 4"
Signature of Engineer/Architect of Record for Project and Date |  |  | 1001.1 to 2000 | 6"
[Affix Engineering/Architect Stamp Here] |  |  | 2000.1 to 3500 | 8"
Fire Flow

## Fixture Value Worksheet
Fixture Flow Value Worksheet
Please call Public Utilities Engineering (239) 252-2583 with any questions.
Enter # of Fixtures of each Fixture Type, per unit, then multiply by appropriate Flow Rate to get Fixture Value
Fixture |  |  |  | Flow Rate |  | # of Fixtures Per Unit |  | Fixture Flow Value
Automatic clothes Washer
Commercial |  |  |  | 3 | x |  | =
Residential |  |  |  | 2 | x |  | =
Bathroom group
As defined in FL Plumbing Code Section 202 (1.6 gpf water closet) |  |  |  | 5 | x |  | =
Bathtub |  |  |  | 4 | x |  | =
Bidet |  |  |  | 2 | x |  | =
Dental unit or cuspidor |  |  |  | 1 | x |  | =
Dishwasher, residential |  |  |  | 2.75 | x |  | =
Drinking fountain |  |  |  | 0.75 | x |  | =
Shower |  |  |  | 3 | x |  | =
Sillcock, hose bibb |  |  |  | 5 | x |  | =
Sink (per faucet)
Kitchen, residential |  |  |  | 2 | x |  | =
Laundry tray |  |  |  | 4 | x |  | =
Lavatory |  |  |  | 2 | x |  | =
Service |  |  |  | 3 | x |  | =
Wash |  |  |  | 2 | x |  | =
Urinal
Standard |  |  |  | 4 | x |  | =
Flushless |  |  |  | 0 | x |  | =
Valve* | Gallons/Flush = |  | x10 |  | x |  | =
Water Closet
Flushometer valve* | Gallons/Flush = |  | x10 |  | x |  | =
Flushometer tank |  |  |  | 1.6 | x |  | =
Tank |  |  |  | 4 | x |  | =
For any fixtures not listed, submit manufacturer's data sheets and enter appropriate description and value:
Other: |  |  |  |  | x |  | =
Other: |  |  |  |  | x |  | =
Other: |  |  |  |  | x |  | =
Other: |  |  |  |  | x |  | =
Other: |  |  |  |  | x |  | =
Total Fixture Value Per Unit =====>
Number of Units with this Fixture Count =====>
Grand Total of Fixture Flow Value (Per Unit Total x Number of Units)** =====>
*Valves are calculated using a flush rate of 10 flushes per minute (according to Florida Plumbing Code). The flow rate is 10 times the gallons per flush. The fixture flow value is calculated as follows: Number of Valves Calculation 1 - 2 Flow Rate times Number of Fixtures. 3 - 10 Flow Rate times two plus two times the Number of Fixtures. 11 or more Flow Rate times Number of Fixtures divided by two.
**Use total Fixture Flow Value on "Table for Estimating Demand" to estimate water meter demand.

## Table for Estimating Demand
Table for Estimating Demand
Please call Public Utilities Engineering (239) 252-2583 with any questions.
SUPPLY SYSTEMS PREDOMINANTLY FOR FLUSH TANKS |  | SUPPLY SYSTEMS PREDOMINANTLY FOR FLUSH VALVES
Load | Demand | Load | Demand
Fixture Flow Value | Gallons per minute | Fixture Flow Value | Gallons per minute
1 | 3 | --- | ---
2 | 5 | --- | ---
3 | 6.5 | --- | ---
4 | 8 | --- | ---
5 | 9.4 | 5 | 15
6 | 10.7 | 6 | 17.4
7 | 11.8 | 7 | 19.8
8 | 12.8 | 8 | 22.2
9 | 13.7 | 9 | 24.6
10 | 14.6 | 10 | 27
11 | 15.4 | 11 | 27.8
12 | 16 | 12 | 28.6
13 | 16.5 | 13 | 29.4
14 | 17 | 14 | 30.2
15 | 17.5 | 15 | 31
16 | 18 | 16 | 31.8
17 | 18.4 | 17 | 32.6
18 | 18.8 | 18 | 33.4
19 | 19.2 | 19 | 34.2
20 | 19.6 | 20 | 35
25 | 21.5 | 25 | 38
30 | 23.3 | 30 | 42
35 | 24.9 | 35 | 44
40 | 26.3 | 40 | 46
45 | 27.7 | 45 | 48
50 | 29.1 | 50 | 50
60 | 32 | 60 | 54
70 | 35 | 70 | 58
80 | 38 | 80 | 61.2
90 | 41 | 90 | 64.3
100 | 43.5 | 100 | 67.5
120 | 48 | 120 | 73
140 | 52.5 | 140 | 77
160 | 57 | 160 | 81
180 | 61 | 180 | 85.5
200 | 65 | 200 | 90
225 | 70 | 225 | 95.5
250 | 75 | 250 | 101
275 | 80 | 275 | 104.5
300 | 85 | 300 | 108
400 | 105 | 400 | 127
500 | 124 | 500 | 143
750 | 170 | 750 | 177
1000 | 208 | 1000 | 208
1250 | 239 | 1250 | 239
1500 | 269 | 1500 | 269
1750 | 297 | 1750 | 297
2000 | 325 | 2000 | 325
2500 | 380 | 2500 | 380
3000 | 433 | 3000 | 433
4000 | 535 | 4000 | 535
5000 | 593 | 5000 | 593

## Sheet1 (hidden)
Demand Range (GPM) |  |  | Meter Size |  | Flush Tanks |  | Flush Valves
|  | 0 |  |  | Load | Demand | Load | Demand
0.1 | to | 30 | 3/4" | Low | 4000 | 535 | 4000 | 535
30.1 | to | 50 | 1" | High | 5000 | 593 | 5000 | 593
50.1 | to | 100 | 1 1/2"
100.1 | to | 160 | 2"
160.1 | to | 450 | 3"
450.1 | to | 1000 | 4"
1000.1 | to | 2000 | 6"
2000.1 | to | 3500 | 8"
Multiple